Thyristor power control exam question

The power supplied to a 50I resistive heating element driven from a single-phase 230IV, 50IHz supply is controlled by a thyristor, which operates with a variable firing angle . The circuit arrangement is shown in the diagram below:

a) For a thyristor firing angle  = 45o, sketch the waveforms of the voltage across and power delivered to the heating element.

b) Derive general algebraic expressions for the average voltage and power supplied to the heating element in terms of .

c) Estimate the firing angle required for the heating element to be supplied with an average power of 500W.

d) The circuit is operated with a firing angle  = 45o, which is obtained using a timer triggered from the supply voltage zero-crossing point and calibrated for a 50IHz supply. In practice the supply voltage magnitude is maintained within ±4% and the frequency within ±3% of the nominal values. Calculate the maximum and minimum value of power supplied to the heating element.

Solution

a)

b)

c)

From the previous part:

where Vpk = 230 * (2 = 325 V ; R = 50 

Try some trial values of :

|  (degrees) | power(W) |
| --- | --- |
| 0.000 | 529.000 |
| 30.000 | 513.747 |
| 40.000 | 494.358 |
| 35.000 | 505.254 |
| 37.000 | 501.193 |
| 38.000 | 499.014 |
| 37.500 | 500.116 |
| 37.600 | 499.898 |
| 37.550 | 500.007 |
| 37.560 | 499.985 |
| 37.555 | 499.996 |

d)

From part b):

With Vpk = 230 * (2 = 325 V ; R = 50  = 45o,

average power = 480 W

The average power is proportional to the square of the supply voltage, so maximum voltage corresponds to maximum power, minimum voltage corresponds to minimum power.

For the firing angle control, if the supply frequency is lower than the expected 50 Hz, the fixed (2.5 ms) timer produces a firing angle less than 45o, but if the frequency is higher, then the firing angle is larger than 45o. The firing angle is proportional to the frequency error, so the maximum firing angle = 45*1.03 = 46.35o and minimum firing angle = 45*0.97 = 43.65o. Substituting these values into the average power expression:

| power (W) | supply voltage (V) |  |
| --- | --- | --- |
|  |  | 220.8 | 230 | 239.2 |
| firing angle (degrees) | 43.65 | 446.8 | 484.8 | 524.4 |
|  | 45 | 443.2 | 480.9 | 520.2 |
|  | 46.35 | 439.5 | 476.9 | 515.8 |

From which:

maximum power = 524 W ; minimum power = 439 W

# Text boxes

230 V,

50 Hz

heating

element

thyristor

voltage and power vs time

0

500

1000

1500

2000

2500

0

45

90

135

180

225

270

315

360

wt (degrees)

voltage (V); power (W)